## Coleambally SF
Generator name | Capacity (MW) | (1) Ancillary service requirements | (2) Level and pattern of network congestion | (3) Impact on timing of expenditure on the network | (4) Impact on interconnector power transfer capability
Coleambally Solar Farm | 150 | There were no new ancillary service contracts in South-western NSW in the 12 months prior to, or following, the commissioning of the Coleambally SF. | The connection of Coleambally SF has increased the generation capacity in South Western NSW. When Coleambally is generating, it has the potential to reduce the power transfer from VNI into Wagga (i.e. reduced utilisation of lines 63) and increase the utilisation of South Western NSW 132kV network lines (i.e. the utilisation of 132kV line 99T from Coleambally to Darlington Point). In the 12 months prior to the connection of Coleambally SF, the constraint equation for voltage stability limitations at Darlington Point constrained for approximately 1117 hours, and in the 12 months following for approx 2060 hours. A new constraint equation for avoiding overloading of line 99T constrained for approximately 448 hours following the connection of Coleambally SF. There are many factors that impact the operation of Darlington Point Voltage constraint equation: - the relative operation of the existing generating units in NSW - NEM dispatch price in NSW and VIC - network outages (planned and unplanned) significantly impact the power transfer limits. All of the above have a far greater impact on the utilisation of VNI and the South Western NSW network compared to a connection of any single SF in South Western NSW. The constraints in the NEM dispatch system can also not specifically by attributed to any single generator. Therefore, it cannot be said that the connection of Coleambally SF has specifically had a material impact on network congestion in the main 330, 220 kV and 132 kV system network, however it is a contributing factor. Localised historical transmission line flows were investigated surrounding Coleambally SF in the south western 132kV network, showing congestion may occur due to Coleambally SF. This is managed by runback and transfer trip schemes in operation and lines were well utilised but did not exceed contingency ratings. | No project timings have been affected by the inclusion of the Coleambally SF. Timing of upgrades to the VNI to NSW interconnector identified in Section 2.1.2 of TransGrid's 2020 TAPR is not specifically affected by the Coleambally SF. | Coleambally SF has negative contribution factor in Darlington Point voltage stability limit equation, which menas it will improve the transfer capability of VNI. The Coleambally SF has no direct impact on the southerly or northerly power transfer capability between QLD and NSW .