## Darlington Point SF
Generator name | Capacity (MW) | (1) Ancillary service requirements | (2) Level and pattern of network congestion | (3) Impact on timing of expenditure on the network | (4) Impact on interconnector power transfer capability
Darlington Point Solar Farm | 275 | There were no new ancillary service contracts in Southern NSW in the 12 months prior to, or following, the commissioning of the Darlington Point SF. | The connection of Darlington Point SF has increased the generation capacity in Southern NSW. When Darlington Point SF is generating, it has the potential to reduce the power transfer from VNI into Wagga (i.e. increased utilisation of lines 63). In the 12 months prior to the connection of Darlington Point SF, the constraint equation for voltage stability limitations at Darlington Point constrained for approximately 2060 hours, and in the 12 months following for approx 805 hours. There are many factors that impact the operation of Darlington Point Voltage constraint equation: - the relative operation of the existing generating units in NSW - NEM dispatch price in NSW and VIC - network outages (planned and unplanned) significantly impact the power transfer limits. All of the above have a far greater impact on the utilisation of VNI and the Southern NSW network compared to a connection of any single SF in Southern NSW. The constraints in the NEM dispatch system can also not specifically by attributed to any single generator. Therefore, it cannot be said that the connection of Darlington Point SF has specifically had a material impact on network congestion in the main 330, 220 kV and 132 kV system network, however it is a contributing factor. Localised historical transmission line flows were investigated surrounding Darlington Point SF in the Southern 132kV network, showing congestion may occur due to Darlington Point SF. This is managed by runback and transfer trip schemes in operation and lines were well utilised but did not exceed contingency ratings.The transfer trips and runback schemes are: thermal schemes for managing overloads of lines 990, 993,99D,99F and 994 and overload of No.1 TX and No.2 TX, and system strength schemes for managing outages of: line 63, Buronga syncons A and B, No.1 TX, No.2 TX and unplanned opening of bus coupler. | No project timings have been affected by the inclusion of the Darlington Point SF. Timing of upgrades to the VNI to NSW interconnector identified in Section 2.1.2 of TransGrid's 2020 TAPR is not specifically affected by the Darlington Point SF. | Limondale No.1 SF has positive contribution factor in N^^N_NIL_1 and N^^N_NIL_2, which menas it may reduce the transfer capability of VNI. The Darlington Point SF has no direct impact on the southerly or northerly power transfer capability between QLD and NSW .
Note on E2: Dragana Hele: Is TAPR2022 or TAPR2022?
Note on F2: Dragana Hele: Gang, please check the hours in the table for constraing equation and statements in regards to the interconnector.