## Sunraysia SF
Generator name | Capacity (MW) | (1) Ancillary service requirements | (2) Level and pattern of network congestion | (3) Impact on timing of expenditure on the network | (4) Impact on interconnector power transfer capability
Suntop SF | 220 | There were no new ancillary service contracts in Central NSW in the 12 months prior to, or following, the commissioning of the Suntop SF. | The connection of Suntop SF has increased the generation capacity in Central NSW. When Suntop SF is generating, it has the potential to increase the utilisation of 132kV line 94K (Parkes to Wellington) and surrounding 132kV lines . In the 12 months prior to the connection of Suntop SF, the constraint equation for avoiding overloading on 94T during system normal is constrained for approximately 0 hours, and in the 12 months following for approximately 843.9 hours. In the 12 months prior to the connection of Suntop SF, the constraint equation for avoiding overloading on 94K during system normal is constrained for approximately 0 hours, and in the 12 months following for approximately 79.4 hours. In the 12 months prior to the connection of Suntop SF, the constraint equation for avoiding overloading on 94K on outage of 998 is constrained for approximately 11 hours, and in the 12 months following for approximately 31.3 hours. There are many factors that impact 94T overloading constraint equation: - the relative operation of the existing generating units in Central NSW - NEM dispatch price in NSW. - network outages (planned and unplanned) significantly impact the power transfer limits. All of the above have a far greater impact on the utilisation of Central NSW network, compared to a connection of any single SF in Central West NSW. The constraints in the NEM dispatch system, can also not specifically by attributed to any single generator. Connection of Suntop SF has had a material impact on network congestion in the main 132 kV system network between Parkes, Wellington, Molong and Orange. If output of Suntop SF is close to its installed capacity, all the surrounding lines in the 132 kV network will be loaded above their contingency rating. Possible congestion of the 132 kV lines surrounding Suntop SF is managed by constraint equation in NEMDE and the following transfer tripping schemes: - Runback schemes to prevent overloads of lines 94T and 94K/1 in the event of changed system conditions or network contingency. | No project timings have been affected by the inclusion of Suntop SF. | Suntop SF has positive contribution factor in constraint equation for overloading of line 94T, which means it will increase loading on this line. Suntop SF is in Central area of NSW and does not have direct influence on either Victoria or Queensland interconnector power capability.